## Battery characteristics
Electrical battery storage comparison | This battery summary table has been drafted by Ricardo EE to help communities consider options for batteries. Every situation will be different and this does not replace the need for technical advice but gives some key characteristics and example use cases for common types of batteries.
Type | Lead Acid (~5.4kWh unit) | Lithium Ion (small 2-16kWh) | Redox Flow Battery (60kW-300kWh) | Lithium Ion (large ~ 1MWh)
Response Time | <second | 10 - 20 ms | 10 - 20 ms | 10 - 20 ms
Storage duration | 20 hours | 30min – 4 hours | 4-8 hours | 30min – 4 hours
System round trip efficiency % | 64% | 86% | 65-75% | 86%
Depth of Discharge (recommended) | 50% | 80% | 100% | 80%
Degradation | Around 4300 cycles to 50% discharge capacity remaining | 80% of initial battery capacity after ~7,000 cycle when cycled within 80% depth of discharge. | 10,000 cycles, no degredation | 80% of initial battery capacity after ~7,000 cycle when cycled within 80% depth of discharge.
Life years | Linked to cycling strategy (depth of discharge and number of cycles) but up to 5 years before deterioration. Potentially >1-2 cycles per day as part of microgrid. | Linked to cycling strategy but 7-15 years <1 cycle per day typical when paired with rooftop solar | No degradation of the cycling medium over time. 20 year life possible with component replacement. Stack 15-20 years - Pumps 6-7 years Potentially >1-2 cycles per day as part of microgrid. | Linked to cycling strategy but 7-15 years 1-1.5 cycles per day typical when providing grid balancing servies. Potentially higher as part of microgrid.
Weight | A single 5.4kWh unit: Weight dry: 100 kg - Weight wet: 143 kg These are can be installed in series. | 40 - 120kg | Weight (Dry): 12800kg Weight (Filled): 28500kg | Weight of battery container: About 30,000 kg Weight of PCS cabinet: About 1,350 kg
Physical dimensions | A single 5.4kWh unit: L - 0.400M - W - 0.27M - H - 0.629M These are can be installed in series. | H: 50.5 cm x W: 34.5 cm x D: 24.5 cm (Moixa 2 & 3kWh Models) H: 115 cm x W: 75 cm x D: 15 cm (Tesla Powerwall 13.5kWh) | 20 ft Hi-Cube Container for the 60kW-300kWh unit L - 5.89M W - 2.35M H - 2.69M | 40ft container - up to 2 MWh storage capacity L - L - 12.05M W - 2.35M H - 2.36M 20ft container - up to 1.2 MWh storage capacity L - 5.89M W - 2.35M H - 2.36M
Operational temperatures | 25°C (-20 to 60°C) | 25°C (-20 to 60°C) | 25°C (-25 to 55°C) | 25°C (–30°C to 50°C)
Capital Cost (£/kWh) | £132 £/kWh | 402 - 1158 £/kWh Unit price linked to power and capacity, with costs between £3,620 and £9,145. Additional installations costs of £1-2,000. | 550-570 £/kWh Units typically sized at 60kW-300kWh (quoted price £205,000 in 2017) and 30kW-150kWh (quoted price £141,000 in 2017). | 204 - 427 £/kWh
O&M costs (% of capex - per year) | 2% |  | 1-2% | 2%
Operation & Maintenance | On-going matenance requirement. Flooded batteries should be checked regularly and electrolyte levels managed. Some tasks may be able to be undertaken by local contractors but a service agreement with the supplier should be povided for. The abiltiy to earn revenue from grid balancing services will be limited by the technology. | Low maintenance requirement and high operational availability. Maintenance contract with manufacturer not a requirement. | The Vanadium medium used by RedT does not degrade over time. Other manufacturers use different mediums which may have different characteristics. Other components will need to be replaced during service lifetime. The expected life of pumps is 6-7 years and the stack is 15-20 years. Some tasks may be able to be undertaken by local contractors but a service agreement with the supplier should be povided for. The abiltiy to earn revenue from grid balancing services will be limited by the technology. | Low maintenance requirement and high operational availability. Maintenance contract with specialist HV electrical contractor required. For participation in grid balancing services a service level contract will need to be agreed with a quick response time, 24-48 hours.
Warranties | Warranty period up to 5 years covering manufacturing defects. | 5-10 year system warranty, linked to remaining capacity of battery, typically 50-80% of design specification. Extended warranties available. | Warranties available, costing quoted as "1-2.5% of CAPEX". Unclear coverage and warranted performance level. | 70-80% of initial capacity available after 10 year warranty or 7000 cycles typical. Warranties are increasingly linked to the use and operation of the battery, including state of charge management clauses. Linked to the minimum available capacity of the battery remaining.
Standards / Regulations | Subject to a range of installation and design standards. Not reviewed in full here and should be secured through the use of an experienced EPC contrator. BS EN IEC 62485-2:2018, Safety requirements for secondary batteries and battery installations | MCS standard sets out the requirements for the supply, design, installation, commissioning and handover of electrical energy storage systems with a maximum power output of 50kW. The standard works in conjunction with the IET Code of Practice for Electrical Energy Storage Systems. The vast majority of small packaged battery products from major manufacturers (e.g. Moixa, Tesla, Powervault, etc) are MCS certified. The MCS standard includes specific provisions for operation in island-mode, necessary for off-grid and micro grid operation. These are detailed in Sections 5.5 and require installation in accordance with BS 7671 and the IET Code of Practice. Grid connection required and should be able to meet requirements of G83 / G59 / G100. | Subject to a range of installation and design standards. Not reviewed in full here and should be secured through the use of an experienced EPC contrator. BS EN IEC 62485-2:2018, Safety requirements for secondary batteries and battery installations | Subject to a range of installation and design standards. Not reviewed in full here and should be secured through the use of an experienced EPC contrator. BS EN IEC 62485-2:2018, Safety requirements for secondary batteries and battery installations
Associated technology | * Batteries * Battery Management System (BMS) * Balance of system (BoS), including container, heating, ventilating and air conditioning (HVAC) and fire suppression * Power Conversion System (PCS), including inverter, switches and breakers and EMS * Metering * Grid connection * Civil and electrical | Packaged battery and micro-inverter unit Fuse box and isolator Comms system Island mode requires a 'backup isolator', such as supplied with Tesla Powerwall products. Not a standard feature. | * Exchanger stack * Fluid tanks * Pumps * Battery Management System (BMS) * Balance of system (BoS), including container, heating, ventilating and air conditioning (HVAC) and fire suppression * Power Conversion System (PCS), including inverter, switches and breakers and EMS * Metering * Grid connection * Civil and electrical | * Battery pack * Battery Management System (BMS) * Balance of system (BoS), including container, heating, ventilating and air conditioning (HVAC) and fire suppression * Power Conversion System (PCS), including inverter, switches and breakers and EMS * Metering * Grid connection * Civil and electrical
Environmental considerations | Lead acid electrolyte can cause environmental damag and is highly hazardous to human health. There are transportation restrictions on flooded lead acid and provisions must be made in case of spillage or leak. Lead is around 99% recyclable. The environmental impact of the production and use of lead-acid batteries for grid-connected domestic systems is negative. Lead acid batteries require many times more raw material than lithium-ion to achieve the same energy storage, making a much larger impact on the environment during the mining process. The lead processing industry is also energy intensive. | Lithium-Ion has a risk of thermal runaway, requiring safety systems to be installed. If the unit is exposed to fire, it may produce poisonous gases. If fire or smoke is detected, the unit must be turned off from the mains. Lithium-Ion systems are not widely recycled and must be disposed of safely. | Safe – No Risk of Thermal Runaway The vanadium solution is low concentration which reduces health and safety risks. Toxicity not a major issue. However spillage risk is an environmental issue and bunding around the installation may be required. The electrolyte does not degrade and can be used again. | Lithium-Ion has a risk of thermal runaway, requiring safety systems to be installed. Containerised systems will include HVAC cooling and fire supression systems. If the unit is exposed to fire, it may produce poisonous gases. Lithium-Ion systems are not widely recycled and must be disposed of safely
Impact of remote (& island) locations | Large lead acid systems are made up of smaller units installed in series. They are typically housed internally. They can be transported by truck. Lifting will be required for installation. System operation can be undertaken remotely. Installation by specialist contractors. Some O&M tasks may be undertaken by local suppliers. | Can be transported in an LGV and lifted manually. To be located in covered and protected location. Installation and some O&M tasks may be undertaken by local suppliers. The abiltiy to earn revenue from grid balancing services may be limited in remote locations. | Redox flow systems typically housed is standard ISO containers and can be transported by truck. Lifting will be required for installation. Additional housed units required for power control systems and inverter. System operation can be undertaken remotely. Installation by specialist contractors. Some O&M tasks may be undertaken by local suppliers, how ever an O&M contract with the manufacturer may be required. | Large Li-ion systems are typically housed is standard ISO containers and can be transported by truck. Lifting will be required for installation. Additional housed units required for power control systems and inverter. System operation can be undertaken remotely. Installation by specialist contractors. Some O&M tasks may be undertaken by local suppliers, however the majority of O&M will need to be with specialist contractors. The abiltiy to earn revenue from grid balancing services may be limited in remote locations.
Advantages | Mature, reliable and well-understood technology. When used correctly, the lead acid battery is durable and provides dependable service. Low maintenance requirements. Low self-discharge. | Packaged systems with micro-invertor can provide balancing to small renewables and back up power supply. High energy density, and relatively low self-discharge. Safe. High round trip efficiency. Low Maintenance requirement. | More than 10,000 cycle life and 100% Depth of Discharge without degradation Safe – No risk of thermal runaway Charge is retained indefinitely with negligible self-discharge over time Electrolyte is 100% recyclable and can be reused over and over again. Optimal Performance with daily usage, coupled with renewables | Able to provide power and energy services at increasinly low cost. Leading technology for <2 hour duration. But cheaper price point means that it is increasinly the technology of choice for 2+ hour duration requirements. High round trip efficiency. High energy density, and relatively low self-discharge. Safe. Low Maintenance requirement.
Limitations | Allows only a limited number of full discharge cycles. It is well suited for standby applications that require only occasional deep discharges. Has been used to provide microgrid balancing but increasingly being displaced by better performing lithium ion. Cannot be stored in a discharged condition. Low energy density. Environmentally unfriendly. The electrolyte and the lead content can cause environmental damage. Transportation restrictions on flooded lead acid. There are environmental concerns regarding spillage in case of an accident. Thermal runaway can occur with improper charging. | Subject to calendar aging, even if not in use. But small relative to cycling degredation. Moderate discharge current. | Low volumetric energy storage capacity. Pumping and electrolyte tanks add to capital costs and maintenance requirements. Promising role in microgrid balancing but has been displaced by better performing lithium ion. Low round trip efficiency. Limited number of suppliers creates a warranty and supply chain risk. Not suitable for small scale applications. Low energy density and large unit sizes. | Subject to calendar aging, even if not in use. But small relative to cycling degredation. Moderate discharge current.
Use case 1: Off grid (individual building / small scale) | Small lithium ion batteries can provide similar services for a longer period, at overall lower cost. | Can provide off-grid power supply, when paired with renewables. | Not applicable | Not applicable
Use case 2: Remote / island microgrid | Lead acid batteries are a popular technology for off-grid communities. However, lithium-ion batteries are being used increasingly due to falling prices and longer lifetime. | Not applicable | Flow batteries have several advantages because they offer long duration services with a long lifetime. However, the market is still small and immature. uptake in off-grid applications is limited particularly as costs relative to lithium ion can be high. | Installed in series can provide longer duration storage to balance microgrid. Better long term perfromance than lead acid/redox flow but depends on requirements.
Use case 3: Co-located with renewables (grid conneted) | There is no economic case for the use of lead-acid batteries for directly grid-connected systems in the UK. Lithium ion batteries provide the services for longer at a lower cost. | Not applicable | There is no economic case for the use of redox flow batteries for directly grid-connected systems in the UK. Lithium ion batteries provide the services for longer at a lower cost. | Lithium ion batteries are well suited for grid scale energy storage. The performance of this technology has been highlighted for the following grid services: Frequency regulation, Peak capacity, Integration with renewable energy sources, Power management.
Use case 4: Direct grid connected (providing grid balancing services) | There is no economic case for the use of lead-acid batteries for directly grid-connected systems in the UK. Lithium ion batteries provide the services for longer at a lower cost. | Not applicable | There is no economic case for the use of redox flow batteries for directly grid-connected systems in the UK. Lithium ion batteries provide the services for longer at a lower cost. | Lithium ion batteries are well suited for grid scale energy storage. The performance of this technology has been highlighted for the following grid services: Frequency regulation, Peak capacity, Integration with renewable energy sources, Power management.
Specifications - References | http://www.windandsun.co.uk/media/1221625/Rolls-4-KS-25P.pdf http://www.esru.strath.ac.uk/Documents/MSc_2015/Breen.pdf Benchmark data provided by the European Association for Energy Storage at: http://ease-storage.eu | https://www.moixa.com/solar-battery/wp-content/uploads/2018/09/0240_Moixa_User_Manual_Email_July_UM001.pdf https://www.tesla.com/en_GB/powerwall https://www.worldenergy.org/assets/downloads/ESM_Final_Report_05-Nov-2019.pdf | https://www.worldenergy.org/assets/downloads/ESM_Final_Rep ort_05-Nov-2019.pdf Benchmark data provided by the European Association for Energy Storage at: http://ease-storage.eu | Ricardo previous projects
Warranties - references | https://www.rollsbattery.com/wp-content/uploads/2019/10/Rolls-Battery-Warranty.pdf | https://www.moixa.com/solar-battery/wp-content/uploads/2018/09/0240_Moixa_User_Manual_Email_July_UM001.pdf https://www.tesla.com/sites/default/files/pdfs/powerwall/powerwall_2_ac_warranty_europe_1-5_english.pdf http://www.powervault.co.uk/wp-content/uploads/2016/09/Powervault-Lithium-ion-10-year-warranty.pdf | Previous communications with RedT - now Invinity Energy Systems - a supplier of redox flow devices. | Ricardo previous projects
Cost - references | Based on prices for Rolls 5000 series lead acid systems: http://www.windandsun.co.uk/products/Batteries/Lead-Acid-Batteries/Rolls-Batteries#6002 | NakedSolar provides a comparison of residential storage systems costs https://nakedsolar.co.uk/storage/ | Previous communications with RedT - now Invinity Energy Systems - a supplier of redox flow devices. | Ricardo price tracking database and https://www.lazard.com/media/451087/lazards-levelized-cost-of-storage-version-50-vf.pdf